## Slide 1: Monitoring and Management of Electrical Systems - per unit values -
05.12.2014
08

## Slide 2: per unit (p.u.) values
In electrical networks with two or more voltage levels, values as branch impedances or voltage values cannot be compared on a common reference.
converting absolute values into per-unit values is, basically, a normalization process, using a base value of choice
example: percent values
are dimensionless – the * symbol is often used: U*, Y*

## Slide 3: Base quantities
In power systems there are four base quantities required to define a per-unit system. These are:
  power (S),
  voltage magnitude (U),
  current (I)
  impedance (Z).
the known basic interdependences are defined:

## Slide 4: Base quantities
Given two of them, all others can be defined using these two. Usually, the base voltage UB and power SB are chosen.
The voltage angle is dimensionless.
Base current and impedance follow as:

## Slide 5: Base change
There are cases when it’s necessary to change the base value, for instance when a system contains transformers and, thus, more than one voltage areas, or when the transformers’ basic parameters are given in producers’ catalogues using different base values (absolute values, percent etc).

## Slide 6: u.r. pentru transformatoare
For the same absolute value of the impedance:
The same applies for admittances.

## Slide 7: The basic p.u. conversion algorithm
Build the one-line diagram of the system
Choose a base value for the power (a multiple of 10 MVA or kVA is recommended).
Place the rated ratios of transformers on the one-line diagram.
Identify the voltage areas of the system, based on the transformer winding voltages.
Choose the base voltage in the first area (the rated voltage in the area is the recommended value).

## Slide 8: The basic p.u. conversion algorithm
Compute the base voltages in the other areas, using the already known base voltages and transformer ratios.
Compute the base impedance in each area.
Compute the per-unit values of impedances, powers and voltages in each area.
Build the one-line diagram in p.u. and eliminate the transformers.
Run the analysis and reconvert the results in absolute values, if necessary.

## Slide 9: Next time…
The Gauss-Seidel load flow method
Thank you !