## Slide 1: Monitoring and Management of Electrical Systems - computer aided analysis of EPS-
31.10.2014
04

## Slide 2: Electric Power Systems

## Slide 3: An optimally operated EPS should:
supply consumers with a guaranteed security level, defined by normatives
keep the main quality indicators of supply (frequency, voltage, harmonics level, phase unbalance)
provide operation with minimal costs (losses)
be in compliance with environmental restrictions

## Slide 4: Dispatchers must:
ensure the balance between the generated and consumed energy
keep the bus voltages in the voltage ranges specified in normatives
keep active and reactive generation of generation units between specified limits
ensure that lines and transformers load does not exceed the limits for long periods of time
take appropriate measures when accident occur, in order to prevent blackouts or limit to the minimum their effects

## Slide 5: EPS monitoring and control
Dispatchers
  know the geographical layout of the monitored system, its network elements and their electrical parameters,
  receive other data collected from the field which tell them the actual operational configuration of the network and its loading condition.
  take decisions
information is processed into specialized analysis software tools, which help in taking the required decisions.

## Slide 6: SCADA functions
power flow studies
state estimation
contingency analysis
optimal power flow
short circuit analysis
distribution-specific functions
load forecast
economic dispatch

## Slide 7: Power flow
input data
output data, results
geographical layout, network elements and their electrical parameters
  the operational configuration
  full electrical description of elements
  loading
bus voltages, magnitude and angle
branch power and current flows
power losses
voltage drops
element loadings
LF analysis algorithm

## Slide 8: Load flow steps
build an one-line diagram
attach electrical parameters to diagram elements
compute the bus admittance matrix
run the analysis algorithm and compute the main state variables (bus voltages, U, θ)
compute the desired auxiliary variables

## Slide 9: 1. Build the one-line diagram

## Slide 10: EPS conventional representation

## Slide 11: EPS conventional representation

## Slide 12: EPS – conventional representation
geographical view | Hand-drawn one-line diagram

## Slide 13: EPS conventional representation

## Slide 14: Sometimes, just data files are used
The IEEE14 bus system

## Slide 15: 2. Attach electrical parameters to elements

## Slide 16: The electrical parameters of a line

## Slide 17: The electrical parameters of a line

## Slide 18: 3. Build the bus admittance matrix

## Slide 19: The [Yn] matrix
A square matrix in which the EPS connections and element parameters are stored
1
2
3
4
5
 | 1 | 2 | 3 | 4 | 5
1 | Y11 | Y12 | 0 | Y14 | 0
2 | Y12 | Y22 | Y23 | 0 | Y25
3 | 0 | Y23 | Y33 | 0 | 0
4 | Y14 | 0 | 0 | Y44 | Y45
5 | 0 | Y25 | 0 | Y45 | Y55

## Slide 20: 4. Compute the load flow

## Slide 21: Direct methods
Topological, linear methods,
  loads are represented using currents
  straightforward methods
  find the exact solution of the problem
  require computing the inverse of large sized complex matrices
    the backward/forward sweep

## Slide 22: Iterative methods
the bus loads are considered non-linear
start with a given approximation of the state variables and determine an approximation of the exact solution applying a series of corrections to the initial approximation
  The Gauss-Seidel method
  The Newton-Raphson method and its variants

## Slide 23: 4. Compute the auxiliary variables

## Slide 24: Auxiliary LF variables
branch active and reactive power flows
branch active and reactive power losses
slack bus active and reactive power in feed
branch voltage drops
branch current flows
element loadings

## Slide 25: Why ?
Bus voltages - magnitude
    In every bus of the system, the voltage magnitude must always remain in a specified range, defined by normatives.
    Working at a too low or too high voltage, electrical equipment ca malfunction, wear out prematurely or become defective.
Bus voltage - angle
    Voltage angle is important for stability studies.
    An important difference in phase angle between two ends of a branch is a sign of heavy loading.
    A breaker can be closed only if the voltage angles at its sides are of close values.

## Slide 26: Why ?
Branch power /current flow - active
    Electrical lines and transformers have physical operating loading margins, which should not be exceeded.
    An overloaded line will have higher losses and, in extreme cases, can suffer of insulation damage or be taken out of service, being tripped by the protection relays. Such contingencies are a main cause for blackouts.
    Equipment and wires are sized for thermal limit current values.

## Slide 27: Why ?
Branch power /current flows - reactive
    Voltage levels in an EPS are closely related to the amount of reactive power flows. Too much reactive power will increase the voltage, while too little reactive power will drop down the voltage.
Active power losses
    Active power losses should be kept at a minimum, because lost power cannot be billed to customers and it's a waste of primary resources.

## Slide 28: Why ?
Branch loading
    Under loaded equipment does not function at its optimum. Lines will generate reactive power through the capacitive effect, raising the voltage levels, and transformers no-load losses do not change.
    Overloaded equipment can be the cause of heavy losses or can be tripped out by protection relays, generating system instability, or can be damaged by the stress. An overloaded system can have frequency stability problems, leading to blackout

## Slide 29: Load flow algorithms main uses
EPS extension or initial design, for proper sizing of the necessary equipment (lines, transformers, protection relays)
the maintenance of operational systems, in approving fixes and upgrades, which should have a minimal effect on the operating conditions of the EPS
post-mortem analyses, based on measurements taken at the occurence of blackouts or other unwanted incidents, for simulating sequences of events and understanding their causes.

## Slide 30: Next time:
EPS elements’ electrical parameters for load flow studies
Thank you !