## Slide 1: Monitoring and Management of Electrical Systems - matrix Yn and general load flow models -
12.11.2014
06

## Slide 2: Load flow steps
build an one-line diagram
attach electrical parameters to diagram elements
compute the bus admittance matrix
run the analysis algorithm and compute the main state variables (bus voltages, U, θ)
compute the desired auxiliary variables

## Slide 3: Load flow computations
Load flow algorithms use the electrical parameters to build equivalent mathematical representations for all EPS elements

## Slide 4: LF equivalent circuits
loads are represented as currents
the transformer ratios are complex
the common ground node 0 is the reference bus
buses 1-4 are independent buses

## Slide 5: LF equivalent circuits
The bus shunt admittances are computed as sums of shunt admittances of EPS elements connected to the bus

## Slide 6: LF equivalent circuits
on the series branches, currents flow from the smaller number order bus to the bigger number order bus, and voltages directions follow the direction of the current
on the shunt branches, currents flow to ground and voltages are directed towards the neutral (ground) bus.
The bus current and voltage vectors are written as:

## Slide 7: LF equivalent circuits
a graph is attached
branches are oriented according to the currents flow

## Slide 8: LF topology equations
Two topology equations can be written

## Slide 9: Matrix [A]
Matrix [A] has a number of rows equal to the number of independent buses in the EPS, and a number of columns equal to the number of EPS branches. Its elements, denoted by aij can be
  0, if branch j does not connect in bus i
  +1 or -1 if branch j is directly connected in bus j, in negative or positive direction
  +Nki sau –Nki if branch j is connected with bus i through the transformer ratio side of a transformer, in positive or negative direction, and directly (via impedance) connected to bus k.

## Slide 10: LF electrical equations
Use admittances
the current on a branch is the product of branch admittance and bus voltage.
In matrix form:

## Slide 11: LF electrical equations
unknown or state variables
the load
bus admittance matrix

## Slide 12: The bus admittance matrix
The bus admittance matrix
    a square matrix,
    number of rows equal to the number of EPS independent buses
    describes electrically and formally the EPS connectivity

## Slide 13: The bus admittance matrix
If the analyzed EPS does not have transformers, is a symmetrical matrix and its elements are computed as follows:
    its main diagonal elements, Yii, have their value equal to the sum of branch admittances connected to bus i
    the elements outside the main diagonal, Yij, have the value equal to the admittance of the branch connecting buses i and j, with minus sign. If no direct branch connection exists between buses i and j, this value is equal to 0.

## Slide 14: The bus admittance matrix
If the EPS has ideal transformers:
    the main diagonal element , Yii, are computed as the sum of elements connected directly, with impedance, to bus i, and the sum of admittances connected through a ideal transformer ratio times the square of the transformer ratio:
    where Li denotes the set of branches connected in bus i and Nki is the ratio of the transformer from branch k connected to bus i. If branch k is connected through impedance with bus i, then Nki=1.

## Slide 15: The bus admittance matrix
If the EPS has ideal transformers:
    the elements outside the main diagonal, Yij, have values equal to the branch connected between buses i and j, with minus sign, times the transformer ratio. If the transformer ratios in the equivalent circuit is at side i, the complex transformer ratio is conjugated.
    If the transformer ratios are complex numbers, the bus admittance matrix is no longer symmetrical.

## Slide 16: The bus admittance matrix

## Slide 17: General LF mathematical models
The i bus in a n independent bus system

## Slide 18: General LF mathematical models
rewrite separately the slack bus equation, and in the other equations the terms where the slack bus voltage appears are separated

## Slide 19: The bus power balance LF model

## Slide 20: The bus power balance LF model
By using the algebraic representation for admittances and the trigonometric representation for voltages:
and separating the real and imaginary parts

## Slide 21: The bus power balance LF model
This complicated equations system cannot be resolved analytically, numerical methods being used instead.
The non-linear expression do not allow the use of direct methods, iterative methods being required.
the non-linear equations system can be written:
f (x) = 0

## Slide 22: Iterative algorithm for solving LF
an initial approximation of the sought solution is generated, x(0), and the iteration counter is set to 1: t = 1
at any step t, with the current approximation x(t), a new x(t+1) approximation is computed, which should be better than the previous approximation
the iterative process continues until a sopping criterion is met
The exact solution it is theoretically found only if an infinite number of iterations is performed. Thus, with a finite number of steps, the found solution will be oanly an approximation.
The best known iterative load flow algorithms are
    the Gauss-Seidel method
    the Newton-Raphson method.

## Slide 23: Next…
Load flow algorithms: Gauss-Seidel
Thank you !