## Slide 1: Monitoring and Management of Electrical Systems - SCADA systems -
31.10.2014
03

## Slide 2: EPS – historical evolution
188x – 193x – local monopolies
193x – now – national or regional monopolies, state or privately owned, vertically integrated
199x – now – deregulated electricity markets
The regulatory framework in the first centralized monopolies was still loose, the major goals being network expansion and profit, rather than system security.

## Slide 3: SCADA
Major blackouts occurring in the USA in the late sixties, with significant social and economic consequences, brought forward to the power systems engineers the problem of system security.
The SCADA/EMS (Supervisory Control and Data Acquisition / Energy Management Systems) concept was born and it is in use until today.

## Slide 4: What is SCADA/EMS?
System state:
    normal, when all constraints and loads are satisfied thorough the system
    emergency, when one or more of the physical operating limits are violated (a collapse is imminent)
    restorative, where one or more of the loads are not met, partial or total blackout, but the partial system is operating in a normal state
The SCADA system provides system engineers with tools to monitor, control, make decisions and issue commands in order to operate the system in these three stages

## Slide 5: SCADA layers
the physical layer, which consists of hardware components installed in the field or at control centres, used to get information about the system state and crucial events occurrence and send back commands from the operators.
the software layer, with specialized computing tools that help the operator make the right decisions, by processing the data collected in the field.

## Slide 6: The architecture of a SCADA/EMS system

## Slide 7: 1. Process sensors
In order to assess the operating state of the whole system or certain equipments, sensors and measuring equipments are installed in the field and send data to the control centers.
    analogue measurements (voltages, power flows, currents);
    discrete values, (ON/OFF status changes)

## Slide 8: 2. Remote Terminal Units (RTU)
RTUs are devices installed in specific locations in the field, which serve as local data gathering units for acquired measurements and for sending back commands to remotely switched equipment at the monitored site.
Modern extensions of RTUs are PLCs, programmable logic controllers, which use microprocessors and programming languages to extend RTU functionalities.

## Slide 9: PowerLogic ION7550
Up to 10 Mbytes of memory
1 pulse output
max 24 digital or analogue inputs
Ethernet port (using the Modbus/TCP/IP protocol)
serial RS 485 / RS 232 port
Internal modem
Alarm notification via email
HTML web page server

## Slide 10: PowerLogic ION7550 - applications
WAGES (water, air, gas, electricity, steam) metering
Integrated utility metering with advanced programmable math functions
Data concentration through multi-port, multi-protocol communications
Equipment status monitoring and control
Programmable set points for out-of-limit triggers or alarm conditions

## Slide 11: RTU 560 units for transmission systems
rack mounting
modular configuration
redundant PSU
up to 16 input/output modules

## Slide 12: RTU 560 features
human machine interface (HMI) with Intel Atom 1.6 Ghz processor, 2 GB of RAM, 16 GB SSD, direct monitor, keyboard and mouse connecting, based on the Windows 7 operating system
simple communication units (CMUs) with Intel 586 133Mhz processor, 64 MB RAM, 128 MB flash memory, serial and Ethernet communication
integrated GPS real time clock.

## Slide 13: 3. Communications
A SCADA system is built for monitoring field installations from a central location, which requires a data communication network.
3 stages of development:
    monolithic
    distributed
    networked

## Slide 14: Monolithic comm structures
when each field RTU was connected with dedicated wires or communication channel to the master station from the control centre;
radio waves, modems and serial communications were used.
IMG: http://www.engineersgarage.com/articles/scada-systems

## Slide 15: Distributed comm structures
LAN distributed computing tasks
IMG: http://www.engineersgarage.com/articles/scada-systems

## Slide 16: Network distributed
geographic fragmentation of the SCADA system over large areas,
local centres connected via WAN and Internet,
the latest advances: the cloud
IMG: http://www.engineersgarage.com/articles/scada-systems

## Slide 17: comm protocols
The first protocols were proprietary, developed by certain vendors and recognized by industry manufacturers.
The most popular: Modbus (1979) by Modicon
    enables communication among approximately 240 devices connected to the same network and identified by unique addresses and sends the results to a computer.

## Slide 18: comm protocols
IEC 60870-5,
IEC 61850
DNP3 (Distributed Network Protocol).
    all have extensions for TCP/IP communication.
For security reasons, SCADA communication networks are built as closed LAN/WAN, preventing direct access from the public Internet.

## Slide 19: 4. SCADA centres
key functions:
  data acquisition
  data logging or archiving: the received data is stored and used subsequently or in real time for system control.
  system monitoring and alarming when control parameters fall out of their normal operation range
  presenting a comprehensive system status overview, ready for operator decision making.

## Slide 20: EMS functions
Load/frequency control:
  because electricity cannot be stored in large quantities, supply must always match the demand.
    If supply exceeds demand, voltage and frequency rise.
    If demand exceeds supply, frequency and voltage drop.
  Voltage variations can damage consumers' equipment, and frequency variation leads to system instability and ultimately blackout.
  Existing SCADA systems provide LFC analysis at 2-10 seconds time interval.

## Slide 21: EMS functions
economic dispatch:
  the existence of a deregulated electricity market aims for commercial profit.
  Based on RTU collected load and generation data, SCADA control centres can provide minimum cost dispatch analyses for intervals of minutes.

## Slide 22: EMS functions
load forecast:
  based on historical data archives, load forecasts can be made for short (hours), medium (1 day-1 week) and long (months, years) intervals

## Slide 23: Security functions
topology processing:
  power systems have built-in redundancies (for instance, lines and transformers operated in parallel).
  an electrical network acts like a living organism, its configuration changes all the time.
  with configuration changes, voltages and power flows change in the system.
  a network topology processor (NTP) determines the actual operating configuration of the system, based on breaker on/off status.

## Slide 24: Security functions
power flow studies:
  based on the actual topology configuration and load/generation scenario, load flow studies compute bus voltages, branch power flows, branch current and active power losses.
  this information is crucial in network extension planning studios, load and generation dispatch, maintenance scheduling and post-mortem analysis.

## Slide 25: Security functions
state estimation:
  gives the same results as a load flow calculation, but uses measurements collected in real-time across the system, giving an operational snapshot of the operating conditions
contingency analysis:
  unexpected line or generator outages can have catastrophic effects on the operating conditions of a power system, leading in extreme cases to blackout

## Slide 26: Security functions
optimal power flow:
  seeks the optimization of a specific objective function, such as minimization of active power losses or bus voltage variation across the system
short circuit analysis:
  for analyzing the fault currents and proper protection setting

## Slide 27: Security functions
distribution-specific functions:
  while transmission systems are considered symmetrical and balanced, distribution systems, especially at low voltage levels, are functioning with unbalanced loads
  require more complex analysis algorithms.

## Slide 28: SCADA limitations
The main drawback is that RTUs collect data by scanning at a 2-10 seconds interval, considered more than sufficient 20 or 30 years ago, but which cannot keep pace with the intermittent nature of renewable sources and rapid development of wide area contingencies.
This low data rate has two major limitations:
    it cannot provide enough data for rapid event analysis
    it cannot provide accurate time stamping and measurement synchronicity.

## Slide 29: Future developments
      modern communication technologies (GSM, 3G, satellite links),
      the geographic information system (GIS),
      Intelligent Electronic Devices
        Digital Fault Recorders (DFRs),
        Digital Protective Relays (DPRs),
        Circuit Breaker Monitors (CBRs),
        Sequence of Event Recorders (SOEs),
        Phasor Measurement Units (PMUs),
The Smart Grid

## Slide 30: Next time:
Computer aided load flow analysis of EPS
Thank you !