## Slide 1
12.12.2014
09
Monitoring and Management of Electrical Systems - the Gauss-Seidel LF method -

## Slide 2: The Gauss-Seidel method
The Gauss-Seidel (GS) load flow method is one of the first developed for computer-aided analysis of EPS steady state, back in the years 1950.
Its simple, yet precise algorithm makes it usable on low performance computer configurations.

## Slide 3: The good and the bad
advantages:
  its algorithm is simple, short and easy to implement using any programming language
  ensures convergence in some special cases where the Newton-Raphson algorithm fails, such as operating states close to instability, or when the initial approximation for the solution is chosen too far from the exact solution.
disadvantages:
  requires a high number of iterations, which grows woth the EPS size
  it is considered that the precision of the results is somewhat lower than for the Newton-Raphson method.

## Slide 4: Still used today….
Paladin Design Base (EDSA)
Power World

## Slide 5: The general mathematical model
For any linear equations system, written as

## Slide 6: The general recurrence rule:

## Slide 7: The general GS model
Starting from an initial approximation [x]0, in an iterative process, a chain of successive approximations [x]1, [x]2, [x]3, … can be computed, which, in certain scenarios, converges to the exact solution.
Usually, matrices [N] and [P] are defined based on the standard decomposition

## Slide 8: The general SG model
[L] (left) is an lower triangular matrix (with thr elements below the main diagonal taken from matrix [A])
[D] is a diagonal matrix, with the elements from the main diagonal equal to the main diagonal elements of matrix [A]
[R] (right) is an lower triangular matrix, with elements above the main diagonal taken from matrix [A].

## Slide 9
Fpr the Gauss-Seidel method, matrices [N] and [P] are:
And the recurrence formula
is thus rewritten as
Which, for a single unknown variable, is written as,
i = 1,…,n

## Slide 10: Example: a 4 equation, 4 variable system

## Slide 11: Example: a 4 equation, 4 variable system
an initial approximation for the solution must be given
all elements from matrix [A] and vector [b] are known

## Slide 12: Example: a 4 equation, 4 variable system
with

## Slide 13
The modified Gauss-Seidel method uses and acceleration procedure which computes first the xit+1 approximation with the standard formula, to which further applies a correction written as:
where 1 and 2 are called acceleration factors.

## Slide 14: Gauss-Seidel for LF
Starting from the general equation:
Any bus current can be written as:
i = 1,…,N; islack

## Slide 15: Gauss-Seidel for LF
Since the load is usually known as active power P and rective power Q, the bus current is rewritten:

## Slide 16: Gauss-Seidel for LF
thus
and the iterative formula:
i = 1,…,N; islack
i = 1,…,N; islack

## Slide 17: The modified G-S for LF
To speed up convergence, acceleration factors can be used
The modified Gauss-Seidel method applies corrections to voltages computed in the current iteration based on their values from the previous iteration and the deviation for two successive iterations:

## Slide 18: Stopping criteria
the deviation of the slack bus power injection computed in two successive iterations below a given threshold:
the maximum deviation of bus voltages computed in two successive iterations below a given threshold:
all deviations between bus voltages computed in two successive iterations fall below a given threshold:

## Slide 19: Next…
The Newton-Raphson LF method
thank you !