## Slide 1
12.12.2014
08
Monitoring and Management of Electrical Systems - the Newton-Raphson LF method -

## Slide 2: Load flow steps
build an one-line diagram
attach electrical parameters to diagram elements
compute the bus admittance matrix
run the analysis algorithm and compute the main state variables (bus voltages, U, θ)
compute the desired auxiliary variables

## Slide 3: The good and the bad
advantages:
  small number of iterations
  high precision
disadvantages:
  high computational effort per iteration, due to the recomputing of the Jacobian and its inverse
  convergence problems, when the initial approximation of the solution is too far from the solution or the problem is ill-conditioned

## Slide 4: The main load flow tool….
Paladin Design Base (EDSA)
Power World

## Slide 5: The main load flow tool….
DIgSILENT Power Factory
Neplan

## Slide 6: The Newton-Raphson method principle
for non-linear equations
starting from an initial approximation of the solution, the function is approximated by its tangent line and the x-intercept of this tangent line it is computed, usually be a better approximation to the function's root than the original guess
compute x(1), x(2), x(3)…
until a stopping criterion
is met
source: Wikipedia

## Slide 7: The Newton-Raphson model
for non-linear equations systems
an initial approximation of the solution,
a vector of functions which defines the non-linear eqns systems,
computed in point [x] from above
the “tangent”:

## Slide 8: The Newton-Raphson model
is a n-sized square matrix, the Jacobian matrix, where any
is the derivative of fi at point xk .

## Slide 9: Newton-Raphson for LF
Given a system with N independent buses, where bus e was designed as slack bus, the apparent electrical power associated to any i bus can be written as:

## Slide 10: Newton-Raphson for LF
If
  admittances are written in algebraic form
  Voltages are written in polar form

## Slide 11: Newton-Raphson for LF
In an all-PQ bus system,
computing Pi and Qi with an initial guess for the voltages, results a difference between the real and computed loads:

## Slide 12: Newton-Raphson for LF
For easing the computation, are replaced with
and the above equations are rewritten as:

## Slide 13: Newton-Raphson for LF
In matrix form:
non-linear system with
2*(N-1) unknowns,
bus voltage mag. and angles
H, J, L and N form de Jacobian
For PV buses, J and L are missing

## Slide 14: Newton-Raphson for LF
Solved iteratively

## Slide 15: The Newton-Raphson algorithm

## Slide 16: Newton-Raphson variants
decoupled
a low correlation between the pairs of components P-U and Q-θ, which is equivalent to small values for the and derivatives, which can be eliminated from the mathematical model.
N, J = 0

## Slide 17: Newton-Raphson variants
fast decoupled
= 0
P-θ
Q-U
constant jacobian

## Slide 18: Load flow steps
build an one-line diagram
attach electrical parameters to diagram elements
compute the bus admittance matrix
run the analysis algorithm and compute the main state variables (bus voltages, U, θ)
compute the desired auxiliary variables

## Slide 19: Branch power flows and losses

## Slide 20: Other
Branch voltage drop
Branch current

## Slide 21: Next…
State estimation in power systems
thank you !